## Important information
Important information
This spreadsheet version of the Template for compliance program compliance tables is intended as a guide to Registered Participants for developing and modifying compliance programs for their generating systems, integrated resource systems, synchronous condenser systems, loads, distribution networks and HVDC networks. It is not an exhaustive list of tests and methodologies, as new, and more effective, approaches may develop over time. Registered Participants should consider the compliance principles set out in Chapter 2 of the Template when applying this table. Chapters 3 and 4 of the Template provide important context for the application of this table and emphasises that participants should exercise their own judgement in determining how best to apply the Template to meet their compliance requirements. In this spreadsheet, underlined terms are defined in section 4.11 of the Template.

## Index
Index of applicable suggested compliance methods
Table No. | Access standard and NER clause | Schedule 5.2 plant (generating systems, integrated resource systems and synchronous condenser systems) |  | Schedule 5.3 plant (loads and distribution networks) | Schedule 5.3a plant (HVDC links)
|  | Synchronous schedule 5.2 plant (e.g Thermal, Hydro, Gas Turbine, Synchronous Condensers) | Asynchronous schedule 5.2 plant (e.g. Wind, Solar, Battery Energy Storage System, Hybrid Battery & Solar) |  | Voltage source converter based HVDC | Line-commutated coverter HVDC
A.1 | S5.2.5.1 Reactive power capability | A.1.1, A.1.2, A.1.3, A.1.S1, A.1.S2, A.1.S3 | A.1.1, A.1.2, A.1.4, A.1.S1, A.1.S2, A.1.S3
A.2 | S5.2.5.2 Quality of electricity generated | A.2.1, A.2.2 | A.2.1, A.2.2
A.3 | S5.2.5.3 Response to frequency disturbances | A.3.1, A.3.2, A.3.4 | A.3.1, A.3.2, A.3.3
A.4 | S5.2.5.4 Response to voltage disturbances | A.4.1, A.4.2, A.4.S1 | A.4.1, A.4.2, A.4.S1
A.5 | S5.2.5.5/S5.2.5.5A Response to disturbances following contingency events / Distrubance ride-through capability | A.5.1, A.5.3, A.5.4 | A.5.2, A.5.3, A.5.4
A.6 | S5.2.5.6 Quality of electricity generated and continuous uninterrupted operation / Response to abnormal voltage quality | A.6.1, A.6.2 | A.6.1, A.6.2
A.7 | S5.2.5.7 Partial load rejection | A.7.1, A.7.2 | A.7.1, A.7.2
A.8 | S5.2.5.8 Protection from power system disturbances | A.8.1, A.8.2 | A.8.1, A.8.2
A.9 | S5.2.5.9 Protection systems that impact on power system security | A.9.1, A.9.S1 | A.9.1, A.9.S1
A.10 | S5.2.5.10 Asynchronous operation of synchronous generating units / Protection to trip plant for unstable operation / Detection and response to unstable operation | A.10.1 | A.10.2
A.11 | S5.2.5.11 Frequency control / Frequency responsiveness and/or governor stability | A.11.1, A.11.2, A.11.3, A.11.4 | A.11.1, A.11.3, A.11.4
A.12 | S5.2.5.12 Stability / Impact on network capability | A.12.1 | A.12.1
A.13 | S5.2.5.13 Voltage and reactive power control / Excitation control system | A.13.2, A.13.3, A.13.4, A.13.S1, A.13.S2 | A.13.1, A.13.S1, A.13.S2
A.14 | S5.2.5.14 Active power control | A.14.1, A.14.2 | A.14.1, A.14.2
A.15 | S5.2.5.15 Short circuit ratio |  | A.15.1
A.16 | S5.2.5.16 Voltage phase angle shift | A.16.1 | A.16.1
A.17 | S5.2.6.1 Remote monitoring | A.17.1 | A.17.2
A.18 | S5.2.6.2 Communications equipment | A.18.1 | A.18.1
A.19 | S5.2.7 Power station / generation auxiliary supplies (S5.2.7) | A.19.1 | A.19.1, A.19.2
A.20 | S5.2.8 Fault level / current (S5.2.8) | A.20.1, A.20.2, A.20.3 | A.20.1, A.20.2, A.20.3
A.21 | Other requirements | A.21.1, A.21.2, A.21.3, A.21.4, A.21.5, A.21.6, A.21.7 | A.21.1, A.21.2, A.21.3, A.21.4, A.21.5, A.21.6, A.21.7
B.1 | S5.3.2 Design standards |  |  | B.1.1
B.2 | S5.3.3 Protection systems and settings |  |  | B.2.1, B.2.S1
B.3 | S5.3.4 Settings of protection and control systems |  |  | B.3.1
B.4 | S5.3.5 Power factor requirements |  |  | B.4.1, B.4.2
B.5 | S5.3.6 Balancing of load currents |  |  | B.5.1, B.5.2
B.6 | S5.3.7 Voltage fluctuations |  |  | B.6.1, B.6.2
B.7 | S5.3.8 Harmonic voltage distortion |  |  | B.7.1, B.7.2
B.8 | S5.3.9 Design requirements for Schedule 5.3 Participants substations |  |  | B.8.1
B.9 | S5.3.10 Load shedding facilities |  |  | B.9.1
B.10 | S5.3.11 Short circuit ratio |  |  | B.10.1 (if an inverter based resource)
B.11 | Other requirements |  |  | B.11.1, B.11.2, B.11.3
C.1 | S5.3a.4.1 Remote monitoring |  |  |  | C.1.1 | C.1.1
C.2 | S5.3a.4.2 Detection and response to unstable operation |  |  |  | C.2.1 | C.2.1
C.3 | S5.3a.4.3 Communications equipment |  |  |  | C.3.1 | C.3.1
C.4 | S5.3a.5 Design standards |  |  |  | C.4.1 | C.4.1
C.5 | S5.3a.6 Protection systems and settings |  |  |  | C.5.1, C.5.S1 | C.5.1, C.5.S1
C.6 | S5.3a.7 Short circuit ratio |  |  |  | C.6.1 | C.6.1
C.7 | S5.3a.8 Reactive power capability |  |  |  | C.7.1 | C.7.2
C.8 | S5.3a.9 Balancing of load currents |  |  |  | C.8.1, C.8.2 | C.8.1, C.8.2
C.9 | S5.3a.10 Voltage fluctuations |  |  |  | C.9.1, C.9.2 | C.9.1, C.9.2
C.10 | S5.3a.11 Harmonic voltage distortion |  |  |  | C.10.1, C.10.2 | C.10.1, C.10.2
C.11 | S5.3a.12 Design requirements for substations |  |  |  | C.11.1 | C.11.1
C.12 | S5.3a.13 Response to disturbances in the power system |  |  |  | C.12.1 | C.12.1
C.13 | S5.3a.14 Distrurbance ride through and response capability / Protection of market network services from power system disturbances |  |  |  | C.13.1, C.13.S1 | C.13.1, C.13.S1
C.14 | S5.3a.15 Voltage and reactive power control |  |  |  | C.14.1, C.14.S1 | C.14.2, C.14.S1
C.15 | S5.3a.16 Active power control |  |  |  | C.15.1, C.15.2 | C.15.1, C.15.2
C.16 | Other requirements |  |  |  | C.16.1 | C.16.1

## A.1
A.1 | Suggested compliance methods for reactive power capability (S5.2.5.1)
As required under S5.2.5.1 in versions 1-243 of the Rules. Testing should consider the voltage range around the mid-point voltage and temperature derating, where relevant under the performance standard. To test the reactive range while minimising impact on network voltages, the reactive output of the plant may be offset by other units or network equipment. This should be arranged in consultation with the NSP and AEMO.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.1.1 | Continuous monitoring, supplemented with active testing | Continuous monitoring of reactive power with reference to voltage or reactive power setpoint | Annual review of performance. | Reactive power is limited at the required level and not limited with the required range.
|  | At rated power output, adjust the reactive power to specified levels. | Every five years when full range has not been demonstrated through continuous monitoring in the previous five years, and after plant change. | Reactive power is limited at the required level and not limited with the required range.
A.1.2 | Active testing, applicable to all plant | At rated power output, adjust the reactive power to specified levels. | Every three years and after plant change. | Be capable of achieving reactive power range, subject to not exceeding network voltage limits.
A.1.3 | Active testing, applicable to synchronous machines | Exercise the over and under excitation limits at as close to rated power output as practical. This may be done in conjunction with step testing of AVR limiters. | Every three years and after plant change. | Be capable of achieving reactive power requirements of the performance standard subject to not exceeding network voltage limits.
A.1.4 | Applicable to wind farms and solar farms where other methods are not practical | Capability will be tested by component; and | Testing of ancillary plant and type testing of sample turbines or solar installation following plant change. | Be capable of achieving performance standard.
|  | Capability will be monitored using SCADA under normal wind and solar farm operation. | Annual review of a selection of events. | Consistency with plant characteristics
A.1.S1 | To be used in conjunction with other methods, if applicable | Verify performance while not generating active power (where applicable under performance standard). | Continuous monitoring or direct measurement every three years and after plant change. | Consistent with performance standard.
A.1.S2 |  | Verify performance while generating units are disconnected (where applicable under performance standard). | Continuous monitoring or direct measurement every three years and after plant change. | Consistent with performance standard.
A.1.S3 | To be used in conjunction with other methods. Applicable to a wide range of generating plant and systems, including capacitor banks, harmonic filters, STATCOMs, and synchronous condensers. | Routine testing of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | Consistency with plant characteristics

## A.2
A.2 | Suggested compliance methods for quality of electricity generated (S5.2.5.2)
As required under S5.2.5.2 in versions 1-243 of the Rules. Performance of the schedule 5.2 plant and its contribution to power quality may need to be separated from the contribution of other plant to show compliance.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.2.1 | Continuous monitoring, applicable to all plant | Continuous monitoring of in-service performance through use of Power Quality Monitors, with alarms for exceedances; and | Continuous monitoring. Specific review every three years and following plant change. | Monitors set against the performance standard are not raising alarms.
|  | Testing and/or calibration of any relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | Consistency with plant characteristics. Important when power quality at the connection point is dependent on ancillary plant or power electronic control systems.
A.2.2 | Periodic measurement, applicable to all plant | Direct measurements using power quality meters to derive: • voltage fluctuation levels; • voltage balance; and • harmonics, flicker and negative phase sequence voltage | Every three years and after plant change. | Achieve performance standard.
|  | Routine testing of any relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | Consistency with plant characteristics. Important when power quality at the connection point is dependent on ancillary plant or power electronic control systems.

## A.3
A.3 | Suggested compliance methods for frequency disturbance responses (S5.2.5.3)
As required under S5.2.5.3 in versions 1-129 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.3.1 | Continuous high-speed monitoring with/without automated assessment tools. Applicable to all plant. | Investigate significant disturbances using continuous high-speed monitoring. | On every event. See significant disturbance example 1. | Event should be reviewed to confirm that the plant trips, as expected. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Investigate major disturbances using continuous high-speed monitoring. | On every event. See major disturbance example 1. | Event should be reviewed to confirm that the plant does not trip. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including: • testing of control system and/or protection system response to disturbances by the injection of simulated frequency / speed control signals; and • Routine tests of electrical / mechanical over speed devices. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.
A.3.2 | Investigation of events where continuous high-speed monitoring is not practical. Applicable to all plant. | Investigating plant trips that occur during significant disturbances. | On every event. See significant disturbance example 1. | Achieve performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including: • testing of control system and/or protection system response to disturbances by the injection of simulated frequency / speed control signals; and • Routine tests of electrical / mechanical over speed devices. | As appropriate to the technology of the relevant sub-system. | As above.
A.3.3 | Continuous high-speed monitoring with Generating Unit (GU) testing. Only applicable to small asynchronous generating units or bidirectional units with digital controls that are distributed and that do not materially differ in terms of their design and settings. Each unit is not material and performance slippage is unlikely. | Verify the modelled performance of a sample of turbines / inverter units. | Following plant change. | Operation over the frequency range specified and agreed in the performance standard.
|  | Verify the performance by testing response to an introduced disturbance. | Type testing and verification every 10 years. | Consistent with the performance standard recorded at the connection point.
|  | Investigate significant disturbances using continuous high-speed monitoring. | On every event. See significant disturbance example 1. | Event should be reviewed to confirm that the plant trips, as expected. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Investigate major disturbances using continuous high-speed monitoring. | On every event. See major disturbance example 1. | Event should be reviewed to confirm that the plant does not trip. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with the performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including: • testing of control system and/or protection system response to disturbances by the injection of simulated frequency / speed control signals; and • Routine tests of electrical / mechanical over speed devices. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.
A.3.4 | Applicable to synchronous generation, where continuous high-speed monitoring is not practical | Performance of relevant sub-systems will be monitored using the following systems under normal machine operation: digital protection relays; other data-logging equipment as required | Every three years by reviewing the response to a disturbance where the system frequency moves outside of the operational frequency tolerance band, and after plant change. | Achieve performance standard.
|  | Routine testing and/or calibration and validation of relevant sub-system performance including: • electrical protection; and • turbine protection. | As appropriate to the technology of the relevant sub-system. | As above.

## A.4
A.4 | Suggested compliance methods for voltage disturbance responses (S5.2.5.4)
As required under S5.2.5.4 in versions 13-251 and S5.2.5.3 in versions 1-12 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.4.1 | Continuous high-speed monitoring with/without automated assessment tools. Applicable to all plant. | Investigate significant disturbances using continuous high-speed monitoring. | On every event. See significant disturbance example 2. | Event should be reviewed to confirm that the plant trips, as expected. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Investigate major disturbances using continuous high-speed monitoring. | At least one major voltage disturbance every three years. See major disturbance example 2. | Event should be reviewed to confirm that the plant maintains continuous uninterrupted operation. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including: • AVR systems; • Auxiliary power systems; and • Protection relays | As appropriate to the technology of the relevant sub-system. | Achieve performance standard. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard. Where possible, testing of auxiliary power systems should include simulated disturbance testing.
A.4.2 | Investigation of events where continuous high-speed monitoring is not practical. Applicable to all plant. | Investigating plant trips that occur during significant disturbances. | On every event. | Achieve performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including: • AVR systems; • Auxiliary power systems; and • Protection relays | As appropriate to the technology of the relevant sub-system. | Consistency with plant characteristics.
A.4.S1 | Applies only to 415 V drives. | With the generator out of service, test the ability of nominated 415 V drives to sustain a specified voltage interruption. | Every four years and after plant change. | Successful ride through of system voltage disturbances, as per the agreed performance standard.

## A.5
A.5 | Suggested compliance methods for contingency event response and disturbance ride-through (S5.2.5.5/S5.2.5.5A)
As required under S5.2.5.5 in versions 13-251 and S5.2.5.5A in versions 234-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.5.1 | Continuous high-speed monitoring for synchronous plant. | Investigate plant trips and significant disturbances using continuous high-speed monitoring | Every event. See significant disturbance example 3. | Confirm plant trips are consistent with performance standard
|  | Analyse major events. | Selection of events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 1. | Event should be reviewed to confirm that the plant meets the performance standard, which may include: • continuous uninterrupted operation • reactive current magnitude • post fault reactive power requirements • post fault active power recovery requirements. Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.
A.5.2 | Continuous high-speed monitoring for asynchronous plant. | Investigate plant trips and significant disturbances using continuous high-speed monitoring | Every event. See significant disturbance example 3. | Confirm plant trips are consistent with performance standard
|  | Analyse major events. | Selection of events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 1. | Event should be reviewed to confirm that the plant meets the performance standard, which may include: • continuous uninterrupted operation • reactive current injection magnitude • positive/negative sequence contribution • reactive current commencement time • reactive current rise time • reactive current settling time or control requirements • post fault reactive power requirements • post fault active power recovery Consistency with models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.
A.5.3 | Investigation of events where continuous high-speed monitoring is not practical. Applicable to all plant. | Investigate plant trips and significant disturbances. | On every event. See significant disturbances example 3. | Achieve performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems including suitable testing to confirm circuit breaker operating times. | As appropriate to the technology of the relevant sub-system. | As above.
A.5.S1 | Applicable to all plant. | Check control system settings against commissioned values and model settings. | Every five years and after plant change. | Control system settings are consistent with models and expected values.

## A.6
A.6 | Suggested compliance methods for abnormal voltage quality (S5.2.5.6)
As required under S5.2.5.6 in versions 13-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.6.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of in-service performance using power quality meters supplied via measurement transformers and transducers with suﬃcient bandwidth. | Investigating plant trips to ensure the trip is not caused by power-quality protection (harmonics or voltage unbalance), unless permitted by the performance standard. Review at least one major event every three years. See major event example 2. | Achieve performance standard.
A.6.2 | Direct measurement and event investigation. Applicable to all plant. | Direct measurements using power quality meters supplied via measurement transformers and transducers with suﬃcient frequency bandwidth to test: • voltage fluctuation levels; • voltage balance; and • harmonics, flicker and negative phase sequence voltage prior to synchronisation; and to ensure protection settings align to the performance standard. | Following plant changes. | Achieve performance standard and ensure protection settings are consistent with the performance standard.
|  | Investigating plant trips to ensure the trip is not caused by power-quality protection (harmonics or voltage unbalance) | Following each event. | Achieve performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.

## A.7
A.7 | Suggested compliance methods for partial load rejection (S5.2.5.7)
As required under S5.2.5.7 in versions 13-243 251 and S5.2.5.4 in versions 1-12 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.7.1 | Monitoring and event investigation. Applicable to all plant. | Measure response of the schedule 5.2 plant to system over-frequency and analyse the unit performance. | On every high frequency event where the frequency moves above the operational frequency tolerance band, or the largest available over frequency event every five years (whichever is more frequent) and after plant change as appropriate to the technology of the relevant sub-system. See major event example 3. | Achieve performance standard.
|  | Investigation of plant trips. | On every event. | As above.
A.7.2 | Routine testing and event investigation. Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including: • Analytical simulation of generator, auxiliary systems and critical protections • Secondary injection testing of critical protection systems; and | As appropriate to the technology of the relevant sub-system. | Simulation demonstrates ride through of load rejection event specified in performance standard.
|  | Assess any plant trip for relationship to load rejection event. | On every event. | Operation over the conditions specified and agreed in the performance standard. Type test permissible where multiple units are involved.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.

## A.8
A.8 | Suggested compliance methods for protection from power system disturbances (S5.2.5.8)
As required under S5.2.5.8 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.8.1 | Continuous high-speed monitoring. Applicable to all plant. | Continuous monitoring using high speed recorders. | On every high frequency event (frequency moves above the operational frequency tolerance band) or largest available over frequency event every five years (whichever is more frequent). See major event example 3. | Consistency with the performance standard and latest plant models is the preferred basis for compliance for 5-yearly testing. Overlaying test data with model responses, using verified models, shows that performance is consistent with past performance, as well as showing the models provided in accordance with clause S5.2.4 are accurate. Where performing model overlays is not practical, this should be substituted with comparison with past performance. If suitable models are not available, the Registered Participant should consider if a model update is required under S5.2.4(d)(2). RMS type models are generally suitable for this test.
|  | Routine testing and/or calibration of relevant sub-systems including: • protection system relays (by secondary injection) • runback schemes, emergency frequency control schemes and trip schemes | As appropriate to the technology of the relevant sub-system. | Protection systems operate in accordance with design and the performance standard.
|  | Investigate protection trips. | On every event. | As above.
A.8.2 | Routine testing and event investigation where continuous high-speed monitoring is not practical. Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including: • protection system relays (by secondary injection) • runback schemes, emergency frequency control schemes and trip schemes | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.
|  | Investigate plant trips. | On every event. | As above.

## A.9
A.9 | Suggested compliance methods for protection systems that impact on power system security (S5.2.5.9)
As required under S5.2.5.9 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.9.1 | Continuous high-speed monitoring. Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including: • protection system testing by secondary injection; • checking of circuit breaker opening times; • redundancy of primary protection systems; • timing of trip signal issued by the breaker fail protection system | As appropriate to the technology of the relevant sub-system. Injection testing at each major overhaul and/or least every five years and after plant change. | That all protection relays operate satisfactorily and to within design tolerance of setting value.
|  | Assessment of protection system performance in the event of protection system operation. | On every event. | That protection system is operated in accordance with design and the performance standard. May use fault recorder data, protection relay records and/or high-speed continuous monitoring.
A.9.S1 | Applicable to all plant. | Verification of database registered protection settings to occur in conjunction with injection testing. | Every five years. | Changes to generating unit control parameters will be controlled such that the performance of the plant is not compromised in relation to the performance standard.

## A.10
A.10 | Suggested compliance methods for detection and response to unstable operation (S5.2.5.10)
As required under S5.2.5.10 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.10.1 | Applicable to synchronous plant. | Routine testing and/or calibration of relevant sub-systems including protection system testing by secondary injection. | As appropriate to the technology of the relevant sub-system. At least every five years and after plant change. | That all protection relays operate satisfactorily and to within design tolerance of setting value.
|  | Assessment of protection system performance in the event of protection system operation or of asynchronous operation. | On every event. | That protection system is operated in accordance with design and the performance standard.
A.10.2 | Applicable to asynchronous plant with instability detection systems. | Routine testing and/or calibration of instability detection system including hierarchy of actions based on trigger conditions. | At least every five years and after plant change. | Instability detection system operates in accordance with design and the performance standard.
|  | Review of instability detection alarms. | Every event. | Instability detection system operates in accordance with design and the performance standard.

## A.11
A.11 | Suggested compliance methods for frequency control (S5.2.5.11)
As required under S5.2.5.11 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.11.1 | Continuous high-speed monitoring. Applicable to all plant. | Monitor in-service performance using high speed frequency data. | After every major disturbance, and a selection of major events, reviewed no less than once every three years. See major disturbance example 1 and major event example 4. | Consistency with the performance standards, as well as consistency with latest plant models for a selection of events at least every five years. Overlaying test data with model responses, using verified models, shows that performance is consistent with past performance, as well as showing the models provided in accordance with clause S5.2.4 are accurate. Where performing model overlays is not practical, this should be substituted with comparison with past performance. If suitable models are not available, the Registered Participant should consider if a model update is required under S5.2.4(d)(2). RMS type models are generally suitable for this clause.
A.11.2 | Event investigation, applicable to synchronous plant. | Assessment of governor system performance, or the performance of other control systems designed to modulate the active power response to a frequency disturbance, during events involving significant variation to system frequency. | After every major disturbance, and a selection of major events, reviewed no less than once every three years. See major disturbance example 1 and major event example 4. | That governor system response is within the tolerance specified by the performance standards. Assessment takes into account inertial response, overall governor droop setting, etc.
A.11.3 | High-speed monitoring with simulation, applicable to all plant. | Analytical simulation of turbine and governor systems, or other control systems designed to modulate active power in response to a frequency disturbance. | Type test permissible where multiple units are involved. | Achieve performance standard.
|  | Assess generator response to disturbances using high speed recording data. | After every major disturbance, and a selection of major events, reviewed no less than once every three years. See major disturbance example 1 and major event example 4. | Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance only if the models are not available.
A.11.4 | Active testing, applicable to all plant. | Step response test of the governor, or other control systems designed to modulate active power in response to a frequency disturbance, to test damping and droop characteristics. | Every four years and after plant change. | Plant performance complies with its performance standard.
|  | Routine calibration tests. | Every four years. | As above.

## A.12
A.12 | Suggested compliance methods for impact on network capability (S5.2.5.12)
As required under S5.2.5.12 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.12.1 | Routine monitoring and testing. Applicable to all plant. | Monitor in-service performance for relevant performance characteristics not otherwise tested. | Following plant changes. | Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance if the models are not available. Registered Participants can only be held responsible for ensuring the performance of their generating system, integrated resource system or synchronous condenser system contributes to meeting their performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems including suitable testing to confirm power system stabiliser performance (if relevant). | As appropriate to the technology of the relevant sub-system. | As above.

## A.13
A.13 | Suggested compliance methods for voltage and reactive power control (S5.2.5.13)
As required under S5.2.5.12 in versions 1-251 of the Rules. • Testing and monitoring regimes should consider control modes and conditions where voltage control may operate differently, including: • Low and high solar irradiance conditions for solar farms • Reactive power on demand mode for solar farms • Low and high State of Charge (SoC) conditions for BESS
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.13.1 | Continuous high-speed monitoring for asynchronous plant, supplemented with active testing. | Analysis of voltage disturbances. | Selection of major events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 5. | Plant performance complies with its performance standard. Models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Analysis of voltage regulation with reference to voltage setpoint and droop (where applicable). | Ongoing monitoring. | Plant performance complies with its performance standard.
|  | Reference steps tests in primary control modes, including steps into reactive limiters. | Every five years and after plant change. | Consistency with the performance standard and latest plant models is the preferred basis for compliance for 5-yearly testing. Overlaying test data with model responses, using verified models, shows that performance is consistent with past performance, as well as showing the models provided in accordance with clause S5.2.4 are accurate. Where performing model overlays is not practical, this should be substituted with a comparison with past performance. If suitable models are not available, the Registered Participant should consider whether a model update is required under clause S5.2.4(d)(2). RMS type models are generally suitable for this clause.
|  | Reference step tests in secondary control modes (where applicable under the performance standard). | Every five years and after plant change. | As above.
A.13.2 | Continuous high-speed monitoring for synchronous plant, supplemented with active testing. | Analysis of voltage disturbances. | Selection of major events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 5. | Plant performance complies with its performance standard. Models provided in accordance with clause S5.2.4 may be used to show compliance with performance standard.
|  | Analysis of voltage regulation with reference to voltage setpoint and droop (where applicable). | Ongoing monitoring. | Plant performance complies with its performance standard.
|  | Synchronised AVR step response tests including step response test of OEL and UEL operation. | Every five years and after plant change. Analogue AVRs should be tested at shorter intervals and testing should include transfer function measurement. | Consistency with the performance standard and latest plant models is the preferred basis for compliance for 5-yearly testing. Overlaying test data with model responses, using verified models, shows that performance is consistent with past performance, as well as showing the models provided in accordance with clause S5.2.4 are accurate. Where performing model overlays is not practical, this should be substituted with comparison with past performance. If suitable models are not available the Registered Participant should consider if a model update is required under S5.2.4(d)(2). RMS type models are generally suitable for this clause.
|  | Reference steps tests in secondary control modes, including steps into reactive limits (where applicable under the performance standard). | Every five years and after plant change. | As above.
|  | AVR and PSS transfer function measurements. | After plant change. | As above.
|  | Unsynchronised AVR step response tests. | After plant change. | As above.
A.13.3 | Active testing of synchronous plant. | Transfer function measurements and step response tests with the unit unsynchronised and at full load. | Every four years and after plant change. Testing frequency may be reduced for modes that are not routinely used to control the output of the schedule 5.2 plant. | Tests should address all control modes specified in the performance standard as commissioned control modes. Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance if the models are not available.
|  | Assess the stability of limiter operation. | Every four years and after plant change for the primary commissioned control mode. | As above.
|  | Monitoring in-service performance or undertake transfer function measurements. | On every event or every four years for the primary commissioned control mode. | As above.
A.13.4 | Active testing of synchronous plant. | AVR step response tests. | Every four years and after plant change for the primary commissioned control mode. | Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance if the models are not available.
|  | AVR step response tst of OEL and UEL operation. | Every four years and after plant change for the primary commissioned control mode. | As above.
|  | AVR and PSS transfer function measurements over required frequency range. | Every four years and after plant change for the primary commissioned control mode. | As above.
A.13.S1 | Monitoring, applicable to all plant. | Performance of relevant sub-systems will be monitored using the following systems: high speed monitors, digital protection relays; other data-logging equipment as required. | As appropriate to the technology of the relevant sub-system. | Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance if the models are not available.
A.13.S2 | Routine checking of control settings, applicable to all plant. | Check control system settings against commissioned values and model settings. | Every five years and after plant change. | Control system settings are consistent with models and expected values.

## A.14
A.14 | Suggested compliance methods for active power control (S5.2.5.14)
As required under S5.2.5.14 in versions 13-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.14.1 | Continuous high-speed monitoring, applicable to all plant. | Continuous monitoring of active power output with reference to dispatch target and required ramp between dispatch intervals | Ongoing. | Achieve performance standard.
|  | Local active power step testing and/or AEMO active power setpoint or semi dispatch testing, as relevant to plant change. | Following plant change. | Achieve performance standard.
A.14.2 | Monitoring using dispatch compliance systems, applicable to all plant. | Monitor non-compliance with dispatch market systems. | Investigate each non-compliance. | Achieve performance standard.
|  | Local active power step testing and/or AEMO active power setpoint or semi dispatch testing, as relevant to plant change. | Following plant change. | Achieve performance standard.

## A.15
A.15 | Suggested compliance methods for short circuit ratio (S5.2.5.15)
As required under S5.2.5.15 in versions 196-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.15.1 | Applicable to all large inverter based resources. | Request AEMO’s opinion on the potential impact of the proposed alteration, in accordance with the System Strength Impact Assessment Guidelines (SSIAG). | Before plant change. | Meet SSIAG requirements.

## A.16
A.16 | Suggested compliance methods for voltage phase angle shift (S5.2.5.16)
As required under S5.2.5.16 in versions 196-233 of the Rules, and S5.2.5.8(b6) in versions 234-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.16.1 | Applicable to all plant. | Model based assessment of ability to meet performance standard. | Before plant change. | Achieve performance standard.
|  | Relay testing of vector shift or similar relay or protective function that acts upon voltage phase angle (where applicable). | At least every five years and after plant change. | Achieve performance standard.

## A.17
A.17 | Suggested compliance methods for remote monitoring (S5.2.6.1)
As required under S5.2.6.2 in versions 13-251 and S5.2.6.3 in versions 1-12 of the Rules, with additional requirements in 4.11.3 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.17.1 | Applicable to all plant. | Calibrate transducers. | Following plant change and every five years. | Confirmation at each end of the communications system by both parties.
|  | Verify the accuracy of transmitted data. | Following plant change and every five years. | As above.
A.17.2 | Applicable to asynchronous plant. | Check SCADA monitored values and farm panel metering. | Every five years. | Achieve performance standard.
|  | Calibrate transducers and metering. | At each major outage or once every five years. | As above.

## A.18
A.18 | Suggested compliance methods for communications equipment (S5.2.6.2)
As required under S5.2.6.2 in versions 13-251 and S5.2.6.3 in versions 1-12 of the Rules, with additional requirements in 4.11.3 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.18.1 | Applicable to all plant. | Confirmation of the availability of communication links, including any backup links with AEMO. | Annual and after plant change. | Achieve performance standard.
|  | Testing of relevant sub-systems including any power backup or UPS system. | As appropriate to the technology of the relevant sub-system. | As above.

## A.19
A.19 | Suggested compliance methods for auxiliary supplies (S5.2.7)
As required under S5.2.7 in versions 13-251 and S5.2.8 in versions 1-12 of the Rules. Only applicable when auxiliary supplies are taken from a location that is different to the schedule 5.2 plant's connection point and a performance standard is established under clause S5.3.5.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.19.1 | Only applicable to auxiliary supplies. | Metering of active and reactive power at the auxiliary supply connection point; and | Every four years and after plant change. | Power factor, quality of supply and protection and control requirements within allowable range / specification.
|  | Testing and/or calibration of any relevant sub-systems including capacitor banks and circuit breakers. | As appropriate to the technology of the relevant sub-system. | Performance to specification.
A.19.2 | Applicable to wind and solar farms with small station service auxiliary load requirements. | Performance will be monitored as part of condition monitoring and maintenance routines. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.

## A.20
A.20 | Suggested compliance methods for fault current (S5.2.8)
As required under S5.2.8 in versions 13-251 and S5.2.9 in versions 1-12 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
A.20.1 | Applicable to all plant. | Monitoring in-service performance during faults near the connection point. | Review following any event. | Calculation confirms fault current contribution.
|  | Review and recalculation of fault levels. | Following plant change. | As above.
|  | Routine testing of any relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.
A.20.2 | Applicable to all plant. | Modelling and simulation of plant characteristics to make sure the plant is capable of meeting agreed standards. | Following plant change. | Achieve performance standard.
|  | Monitoring of plant contribution on fault event. | Review following any event. | As above.
A.20.3 | Applicable to all plant. | Performance of relevant sub-systems will be monitored using the following systems: digital protection relays; other data-logging equipment as required. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.
|  | Where recorded data is available, comparison to be made of measured fault currents and computer simulations. | Following a fault. | Consistency of operation with the latest plant model provided in accordance with clause S5.2.4 if the models are available; OR consistency with past performance if the models are not available.
|  | Review and recalculation of fault levels. | Following plant change. | As above.

## A.21
A.21 | Other requirements
Technical requirements, in addition to those under Schedule 5.2, may apply to Schedule 5.2 plant. Where applicable, these requirements should be considered in the design of an overall compliance program. The hyperlinks in the footnotes below are current, as of the time of the publication of this Template. Where documents are updated or revised following the publication of this Template, Registered Participants should refer to the most recent version of the documents listed below.
Method number | Other requirement | Reference
A.21.1 | Frequency Control Anciliary Service (FCAS) requirements | Refer to the Market Ancillary Service Specification (MASS).
A.21.2 | Non-market ancillary service requirements | Refer to the power system operating procedure SO_OP_3708.
A.21.3 | Primary Frequency Response (PFR) requirements | Refer to the Primary Frequency Response Requirements (PFRR).
A.21.4 | Remote monitoring equipment requirements | Refer to the Power System Data Communications Standard (PSDCS).
A.21.5 | Communications failure requirements | Refer to the Communication System Failure Guidelines (CSFG).
A.21.6 | Dispatch requirements | Refer to the power system operating procedure SO_OP_3705.
A.21.7 | VAR dispatch requirements | Refer to the Guide to VAR Dispatch.

## B.1
B.1 | Suggested compliance method for design standard requirements (S5.3.2)
As required under S5.3.2 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.1.1 | Applicable to all plant. | Review plant changes against the design standard requirements. | Before plant change. | Plant change meets all design requirements.

## B.2
B.2 | Suggested compliance method for protection systems and settings (S5.3.3)
As required under S5.3.3 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.2.1 | Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including: • protection system testing by secondary injection; • checking of circuit breaker opening times; • redundancy of primary protection systems; and • timing of trip signal issued by the breaker fail protection system | As appropriate to the technology of the relevant sub-system. Injection testing at least every five years and after plant change. | That all protection relays operate satisfactorily and to within design tolerance of setting value.
|  | Assessment of protection system performance in the event of protection system operation. | On every event. | That protection system is operated in accordance with design and the performance standard. May use fault recorder data, protection relay records and/or high-speed continuous monitoring.
B.2.S1 | Applicable to all plant. | Verification of database registered protection settings to occur in conjunction with injection testing. | Every five years. | As above.

## B.3
B.3 | Suggested compliance method for settings of protection and control systems (S5.3.4)
As required under S5.3.4 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.3.1 | Applicable to all plant. | Document settings changes and communication with Network Service Provider on settings changes. | Ongoing. | Settings changes managed in accordance with requirements.

## B.4
B.4 | Suggested compliance method for power factor (S5.3.5)
As required under S5.3.5 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.4.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of power factor. | Review of data at least every three years. | Power factor within allowable range.
B.4.2 | Periodic measurement. Applicable to all plant. | Direct measurement of power factor. | Every three years and following plant change. | Power factor within allowable range.

## B.5
B.5 | Suggested compliance methods for balancing of load currents (S5.3.6)
As required under S5.3.6 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.5.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of current unbalance. | Review of data at least every three years. | Current unbalance within allowable range.
B.5.2 | Periodic measurement. Applicable to all plant. | Direct measurement of current unbalance. | Every three years and following plant change. | Current unbalance within allowable range.

## B.6
B.6 | Suggested compliance methods for voltage fluctuations (S5.3.7)
As required under S5.3.7 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.6.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of in-service voltage fluctuations using power quality monitors. | Review of data at least every three years. | Voltage fluctuations within allowable range.
B.6.2 | Periodic measurement. Applicable to all plant. | Direct measurements using power quality meters to derive voltage fluctuation levels. | Every three years and following plant change. | Voltage fluctuations within allowable range.

## B.7
B.7 | Suggested compliance methods for harmonic voltage distortion (S5.3.8)
As required under S5.3.8 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.7.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring in-service performance using power quality meters supplied via measurement transformers and transducers with sufficient bandwidth. | Review of data at least every three years. | Harmonic voltage distortion within allowable range.
B.7.2 | Periodic measurement. Applicable to all plant. | Direct measurements using power quality meters supplied via measurement transformers and transducers with sufficient bandwidth to measure harmonic voltage distortion. | Every three years and following plant change. | Harmonic voltage distortion within allowable range.

## B.8
B.8 | Suggested compliance method for substation design requirements (S5.3.9)
As required under S5.3.9 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.8.1 | Applicable to all plant. | Review plant changes against the design standard requirements. | Before plant change. | Plant change meets all design requirements.

## B.9
B.9 | Suggested compliance method for load shedding facilities (S5.3.10)
As required under S5.3.10 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.9.1 | Applicable to all plant. | • Routine testing and/or calibration of relevant sub-systems including, where applicable: • testing of under frequency load shedding relays by the injection of simulated frequency signals; and • testing of under voltage load shedding relays by the application of simulated secondary voltages. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.

## B.10
B.10 | Suggested compliance method for short circuit ratio (S5.3.11)
As required under S5.3.11 in versions 196-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
B.10.1 | Applicable to all inverter based resources. | Request AEMO’s opinion on the potential impact of the proposed alteration, in accordance with the System Strength Impact Assessment Guidelines (SSIAG). | Before plant change. | Meet SSIAG requirements.

## B.11
B.11 | Other requirements
Technical requirements, in addition to those under Schedule 5.3, may apply to Schedule 5.3 plant. Where applicable, these requirements should be considered in the design of an overall compliance program. The hyperlinks in the footnotes below are current, as of the time of the publication of this Template. Where documents are updated or revised following the publication of this Template, Registered Participants should refer to the most recent version of the documents listed below.
Method number | Other requirement | Reference
B.11.1 | Frequency Control Anciliary Service (FCAS) requirements | Refer to the Market Ancillary Service Specification (MASS).
B.11.2 | Non-market ancillary service requirements | Refer to the power system operating procedure SO_OP_3708.
B.11.3 | Dispatch requirements | Refer to the power system operating procedure SO_OP_3705.

## C.1
C.1 | Suggested compliance method for remote monitoring (S5.3a.4.1)
As required under S5.3a.4.1 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.1.1 | Applicable to all plant. | Verify the accuracy of transmitted data. | Following plant change and every five years. | Confirmation at each end of the communications system by both parties.
|  | Routine testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | Confirmation of monitoring system accuracy.

## C.2
C.2 | Suggested compliance method for detection and response to unstable operation (S5.3a.4.2)
As required under S5.3a.4.2 in versions 234-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.2.1 | Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including instability detection system and hierarchy of actions based on trigger conditions. | At least every five years and after plant change. | Instability detection system operates in accordance with design and the performance standard.
|  | Review of instability detection alarms. | Every event. | Instability detection system operates in accordance with design and the performance standard.

## C.3
C.3 | Suggested compliance method for communications equipment (S5.3a.4.3)
As required under S5.3a.4.3 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.3.1 | Applicable to all plant. | Confirmation of the availability of communication links, including any backup links with AEMO. | Annual and after plant change. | Achieve performance standard.
|  | Testing of relevant sub-systems including any power backup or UPS system. | As appropriate to the technology of the relevant sub-system. | As above.

## C.4
C.4 | Suggested compliance method for design standards (S5.3a.5)
As required under S5.3a.5 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.4.1 | Applicable to all plant. | Review plant changes against the design standard requirements. | Before plant change. | Plant change meets all design requirements.

## C.5
C.5 | Suggested compliance methods for protection systems and settings (S5.3a.6)
As required under S5.3a.6 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.5.1 | Applicable to all plant. | Routine testing and/or calibration of relevant sub-systems including: • protection system testing by secondary injection; • checking of circuit breaker opening times; • redundancy of primary protection systems; and • timing of trip signal issued by the breaker fail protection system. | As appropriate to the technology of the relevant sub-system. Injection testing at least every five years and after plant change. | That all protection relays operate satisfactorily and to within design tolerance of setting value.
|  | Assessment of protection system performance in the event of protection system operation. | On every event. | That protection system is operated in accordance with design and the performance standard. May use fault recorder data, protection relay records and/or high-speed continuous monitoring.
C.5.S1 | Applicable to all plant. | Verification of database registered protection settings to occur in conjunction with injection testing. | Every five years. | As above.

## C.6
C.6 | Suggested compliance method for short circuit ratio (S5.3a.8)
As required under S5.3a.7 in versions 196-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.6.1 | Applicable to all inverter based resources. | Request AEMO’s opinion on the potential impact of the proposed alteration, in accordance with the System Strength Impact Assessment Guidelines (SSIAG). | Before plant change. | Meet SSIAG requirements.

## C.7
C.7 | Suggested compliance methods for reactive power capability (S5.3a.8)
As required under S5.3a.8 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.7.1 | Applicable to voltage source converter based HVDC. | Continuous monitoring of reactive power at the connection points. | Annual review of performance. | Reactive power is limited at the required level and not limited with the required range.
|  | At rated power output, adjust the reactive power at the connection point to specified levels (at both connection points). | Every five years when full range has not been demonstrated through continuous monitoring in the previous five years. After plant change. | Be capable of achieving reactive power range, subject to not exceeding network voltage limits.
C.7.2 | Applicable to line-commutated converter (LCC) HVDC without dynamic reactive power control. | Continuous monitoring of reactive power at the connection points. | Annual review of performance. | Reactive power is maintained with the required range.
|  | Routine testing of relevant sub-systems including harmonic filters, capacitor banks and their control systems. | As appropriate to the technology of the relevant sub-system. | Performance consistent with design.

## C.8
C.8 | Suggested compliance methods for balancing of load currents (S5.3a.9)
As required under S5.3a.9 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.8.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of current unbalance. | Review of data at least every three years. | Current unbalance within allowable range.
C.8.2 | Periodic measurement. Applicable to all plant. | Direct measurement of current unbalance. | Every three years and following plant change. | Current unbalance within allowable range.

## C.9
C.9 | Suggested compliance methods for voltage fluctuations (S5.3a.10)
As required under S5.3a.10 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.9.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of in-service voltage fluctuations using power quality monitors. | Review of data at least every three years. | Voltage fluctuations within allowable range.
C.9.2 | Periodic measurement. Applicable to all plant. | Direct measurements using power quality meters to derive voltage fluctuation levels. | Every three years and following plant change. | Voltage fluctuations within allowable range.

## C.10
C.10 | Suggested compliance methods for voltage fluctuations (S5.3a.11)
As required under S5.3a.11 in versions 1-251 of the Rules. Performance of the HVDC network and its contribution to power quality may need to be separated from the contribution of others to show compliance.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.10.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring in-service performance using power quality meters supplied via measurement transformers and transducers with sufficient bandwidth. | Review of data at least every three years and following plant change. | Harmonic voltage distortion within allowable range.
C.10.2 | Periodic measurement. Applicable to all plant. | Direct measurements using power quality meters supplied via measurement transformers and transducers with sufficient bandwidth to measure harmonic voltage distortion. | Every three years and following plant change. | Harmonic voltage distortion within allowable range.

## C.11
C.11 | Suggested compliance method for substation design requirements (S5.3a.12)
As required under S5.3a.12 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.11.1 | Continuous monitoring. Applicable to all plant. | Review plant changes against the design standard requirements. | Before plant change. | Plant change meets all design requirements.

## C.12
C.12 | Suggested compliance method for power system disturbance response (S5.3a.13)
As required under S5.3a.13 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.12.1 | Applicable to all plant. | Investigate significant disturbances for voltage and frequency using continuous high-speed monitoring. | On every event. See significant disturbance examples 1 and 2. | Event should be reviewed to confirm that the plant trips, as expected. Consistency with models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Investigate major disturbances for voltage and frequency using continuous high-speed monitoring. | At least one major disturbance for voltage and one major disturbance for frequency every three years. See major disturbance examples 1 and 2. | Event should be reviewed to confirm that the plant maintains continuous uninterrupted operation. Consistency with models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Routine testing and/or calibration of relevant sub-systems including testing of control system and/or protection system response to disturbances by the injection of simulated frequency / speed control signals. | As appropriate to the technology of the relevant sub-system. | Achieve performance standard.

## C.13
C.13 | Suggested compliance method for disturbance ride through capability (S5.3a.14)
As required under S5.3a.14 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.13.1 | Applicable to all plant. | Investigate plant trips and significant disturbances using continuous high-speed monitoring. | On every event. See significant disturbance example 3. | Confirm plant trips are consistent with performance standard. Consistency with models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Analyse major events. | Selection of events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 1. | Event should be reviewed to confirm that the plant meets the performance standard for behaviour during faults and post fault. Consistency with models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.
C.13.S1 | Applicable to all plant. | Check control system settings against commissioned values and model settings. | Every five years and after plant change. | Control system settings are consistent with models and expected values.

## C.14
C.14 | Suggested compliance methods for voltage and reactive power control (S5.3a.15)
As required under S5.3a.15 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.14.1 | Applies to voltage source converter based HVDC. | Analysis of voltage disturbances using high speed data. | Selection of major events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major events example 5. | Plant performance complies with its performance standard. Models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Reference steps tests including steps into reactive limiters. | Every five years and after plant change. | Consistency with the performance standard and latest plant models is the preferred basis for compliance for 5-yearly testing. Overlaying test data with model responses, using verified models, shows that performance is consistent with past performance, as well as showing the models provided in accordance with clause S5.3a.1 are accurate. Where performing model overlays is not practical, this should be substituted with comparison with past performance. Where suitable models are not available, the Registered Participant should consider if a model update is required. RMS type models are generally suitable for this clause.
|  | Routine monitoring and testing and/or calibration of relevant sub-systems. | As appropriate to the technology of the relevant sub-system. | As above.
C.14.2 | Applies to Line Commutated Converter (LCC) HVDC without dynamic reactive power control. | Analysis of voltage disturbances using high speed data. | Selection of major events reviewed no less than once every three years. Events should be chosen to test the range of performance standard requirements. See major event example 5. | Plant performance complies with its performance standard. Models provided in accordance with clause S5.3a.1 may be used to show compliance with performance standard.
|  | Routine testing of relevant sub-systems including harmonic filters, capacitor banks and their control systems. | As appropriate to the technology of the relevant sub-system. | Performance consistent with design.
C.14.S1 | Applicable to all plant. | Check control system settings against commissioned values and model settings. | Every five years and after plant change. | Control system settings are consistent with models and expected values.

## C.15
C.15 | Suggested compliance methods for active power control (S5.3a.16)
As required under S5.3a.16 in versions 1-251 of the Rules.
Method number | Type of method and applicability | Method description | Suggested assessment frequency | Basis for compliance assessment
C.15.1 | Continuous monitoring. Applicable to all plant. | Continuous monitoring of active power output with reference to dispatch target and required ramp between dispatch intervals. | Ongoing. | Achieve performance standard.
|  | Local active power step testing and/or AEMO active power setpoint testing, as relevant to plant change. | Following plant change. | Achieve performance standard.
C.15.2 | Monitoring using dispatch compliance systems. Applicable to all plant. | Monitor non-compliance with dispatch market systems. | Investigate each non-compliance. | Achieve performance standard.
|  | Local active power step testing and/or AEMO active power setpoint testing, as relevant to plant change. | Following plant change. | Achieve performance standard.

## C.16
C.16 | Other requirements
Technical requirements, in addition to those under Schedule 5.3a, may apply to schedule 5.3a plant. Where applicable, these requirements should be considered in the design of an overall compliance program. The hyperlinks in the footnotes below are current, as of the time of the publication of this Template. Where documents are updated or revised following the publication of this Template, Registered Participants should refer to the most recent version of the documents listed below.
Method number | Other requirement | Reference
C.16.1 | Dispatch requirements | Refer to the power system operating procedure SO_OP_3705.