## Table to assist development of generator compliance programs

| Performance Standard/Rules/Code Provision | Suitable testing and monitoring methodology | Frequency | Notes | Basis for compliance assessment |
| --- | --- | --- | --- | --- |
| Reactive Power Capability (as required under S5.2.5.1 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: At rated power output, adjust the reactive power capability to specified levels | Every 3 years and after plant change | Directly Measurable. Applies to synchronous and conventional plant. | Achieve reactive power requirements of the performance standard |
|  | Method 2: Exercise the over and under excitation limits at as close to rated power output as practical | Every 3 years and after plant change | Directly Measurable. Applies to synchronous and conventional plant. | Achieve reactive power requirements of the performance standard |
|  | Method 3: Step testing of AVR limiters | Every 3 years and after plant change | Applies to conventional plant | Achieve reactive power requirements of the performance standard |
|  | Method 4: - Capability will be tested by component | Testing of ancillary plant and type testing of sample turbines following plant change | Applies to wind farms plant | Achieve performance standard |
|  | - Capability will be monitored using SCADA under normal wind farm operation | Annual review of a selection of events |  | Consistency with plant characteristics |
|  | Method 5: Routine testing of relevant sub-systems | As appropriate to the technology of the relevant sub-system | Applicable to a wide range of generating plant and systems | Consistency with plant characteristics |
| Power Factor Requirements (as required under S5.3.5 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Direct measurement and calculation of power factor when not generating | Every 3 years and following plant change | Only applies where there is a circuit breaker, allowing auxiliary supply to be drawn through the main connection point | Actual capability directly demonstrated |
| Quality of Electricity Generated (as required under S5.2.5.2 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Direct measurements using power quality meters to derive: - voltage fluctuation levels - voltage balance - harmonics, flicker and negative phase sequence voltage prior to synchronisation | Following plant change | Performance of generator and its contribution to power quality needs to be separated from the contribution of others. | Achieve performance standard or demonstrate consistency with plant characteristics used in determining original compliance |
|  | - Routine testing of any relevant sub-systems | As appropriate to the technology of the relevant sub-system | Important when power quality at the connection point is dependent on ancillary plant of power electronic control systems. |  |
|  | Method 2: - Monitoring in-service performance through use of Power Quality Monitors | Routine monitoring Specific review every 3 years and following plant change |  | Monitors set against the performance standard are not raising alarms. Consistency with plant characteristics (no deterioration). |
|  | - Testing of any relevant sub-systems | As appropriate to the technology of the relevant sub-system | Important when power quality at the connection point is dependent on ancillary plant of power electronic control systems. | Consistency with plant characteristics. |
| Response to Frequency Disturbances (as required under S5.2.5.3 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Investigating plant trips that occur during significant frequency disturbances | On every event |  | Achieve performance standard |
|  | - Routine testing of relevant sub-systems including: - testing of control system response to disturbances by the injection of simulated frequency / speed control signals - Routine tests of electrical / mechanical over speed devices | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 2: - Investigating system performance using high speed data recorders | Every event where the plant trips and disturbances where the frequency moves out of the operational frequency tolerance band | Appropriate to use where high speed monitors are available and models have been used in establishing compliance | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance only if the models are not available |
|  | - Routine testing of relevant sub-systems including: - testing of control system response to disturbances by the injection of simulated frequency / speed control signals - Routine tests of electrical / mechanical over speed devices | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 3: - Verify the modelled performance of a sample of turbines | Following plant change | Only applicable to small asynchronous generators with digital controls that are aggregated. | Operation over the frequency range specified and agreed in the Generator Performance Standard |
|  | - Verify the performance at the connection point by testing response to an introduced disturbance | Type testing and verification every 10 years | Each unit is not material and performance slippage is unlikely. |  |
|  | - Continuous monitoring (high speed) of performance at the connection point |  | Appropriate to use where high speed monitors are available and models have been used in establishing compliance. |  |
|  | - Routine testing of relevant sub-systems including: - testing of control system response to disturbances by the injection of simulated frequency / speed control signals - Routine tests of electrical / mechanical over speed devices | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 4: - Performance of relevant sub-systems will be monitored using the following systems under normal machine operation: digital protection relays; other data-logging equipment as required | Every 3 years |  | Achieve performance standard |
|  | - Routine testing and validation of relevant sub-system performance including: - electrical protection; and - turbine protection | As appropriate to the technology of the relevant sub-system |  |  |
| Response to Voltage Disturbances (as required under: S5.2.5.3 in versions 1-12 of the Rules, and S5.2.5.4 in versions 13-30 of the Rules; and S5.2.5.3 in the initial Code, and all amended versions of the Code) | Method 1: - Investigating plant trips that occur during significant voltage disturbances | On every event |  |  |
|  | - Routine testing of relevant sub-systems including: - AVR systems - Auxiliary power systems - Protection relays | As appropriate to the technology of the relevant sub-system |  | Consistency with plant characteristics |
|  | Method 2: - Continuous high speed monitoring | On every event where the plant trips or on at least one major voltage disturbance every 3 years | Appropriate to use where high speed monitors are available and models have been used in establishing compliance. | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance only if the models are not available |
|  | - Routine testing of relevant sub-systems including: - AVR systems - Auxiliary power systems - Protection relays | As appropriate to the technology of the relevant sub-system | Where possible, testing of auxiliary power systems should include simulated disturbance testing. |  |
|  | Method 3: - With the generator out of service, test the ability of nominated 415 V drives to sustain a specified voltage interruption | Every 4 years | Applies only to 415 V drives. | Successful ride through of system voltage disturbances, as per the agreed performance standard |
|  | - In-service monitoring and investigation of any occurrence of a plant trip which may have been associated with a system voltage disturbance | On every event | This type of monitoring will be acceptable only if high speed monitoring is not available. |  |
| Response to Disturbances following Contingency Events (as required under S5.2.5.5 in versions 13-30 of the Rules) | Method 1: Direct testing by instigating a network trip | Following plant changes | Preferred method where possible and where risks can be managed | Achieve performance standard |
|  | Method 2: - Investigate plant trips that occur during or immediately following major system events | On every event |  | Achieve performance standard |
|  | - Routine monitoring and testing of relevant sub-systems including suitable testing to confirm circuit breaker operating times | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 3: - Continuous monitoring using high speed recorders | On disturbances when the plant trips or at least one major event every 3 years | Appropriate to use where high speed monitors are available and models have been used in establishing compliance | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance only if the models are not available |
|  | - Routine monitoring and testing of relevant sub-systems | As appropriate to the technology of the relevant sub-system |  |  |
| Quality of Electricity Generated and Continuous Uninterrupted Operation (as required under S5.2.5.6 in versions 13-30 of the Rules) | Method 1: - Direct measurements using power quality meters to test: - voltage fluctuation levels - voltage balance - harmonics, flicker and negative phase sequence voltage prior to synchronisation and to ensure protection settings align to the performance standard | Following plant changes |  | Achieve performance standard and ensure protection settings are consistent with the performance standard. |
|  | - Investigating plant trips to ensure the trip is not caused by power-quality protection (harmonics or voltage unbalance) | Following each event |  | Achieve performance standard. |
|  | - Routine monitoring and testing of any relevant sub-systems | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 2: Monitoring in-service performance using appropriate metering | On disturbances when the plant trips including at least one major event every 3 years | Appropriate to use where suitable metering is available | Consistency of operation with plant performance specifications |
| Partial Load Rejection (as required under: S5.2.5.4 in versions 1-12 of the Rules, and S5.2.5.7 in versions 13-30 of the Rules; and S5.2.5.4 of the initial Code, and all amended versions of the Code) | Method 1: - Measure response of the generator to system over-frequency and analyse the unit performance |  | Directly measurable | Achieve performance standard |
|  | - Investigation of plant trips | On every event |  |  |
|  | Method 2: - Routine testing of relevant sub-systems including: - Analytical simulation of generator, auxiliary systems and critical protections - Secondary injection testing of critical protection systems | As appropriate to the technology of the relevant sub-system |  | Simulation demonstrates ride through of load rejection event specified in Performance Standard. |
|  | - Assess any plant trip for relationship to load rejection event | On every event | Type Test permissible where multiple units are involved | Operation over the conditions specified and agreed in the Generator Performance Standard. |
|  | Method 3: - Response to partial load rejection to be assessed by in-service performance |  |  | Achieve performance standard. |
|  | - Test for correct operation of turbine overspeed trips | Every 4 years | Overspeed protection checked off-line after major overhauls | That turbine trip operates to within acceptable tolerance of nominal trip setting for overspeed protection. |
| Protection from Power System Disturbances (as required under S5.2.5.8 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Continuous monitoring using high speed recorders |  | Appropriate to use where high speed monitors are available and models have been used in establishing compliance | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available. |
|  | - Routine testing of relevant sub-systems including applicable protection relays | As appropriate to the technology of the relevant sub-system |  | That protection system operated in accordance with design and the Performance Standard. |
|  | - Investigate unit electrical protection trips | On every event |  |  |
|  | Method 2: - Routine testing of relevant sub-systems including: - Injection of simulated signals (secondary injection) to demonstrate correct operation of the protection - Repair or recalibrate protection relays as required | As appropriate to the technology of the relevant sub-system |  | Achieve performance standard |
|  | - Investigate plant trips | On every event |  |  |
|  | Method 3: - Performance is monitored, in-service | At each major overhaul; and/or every 5 years by routine functional testing of unit electrical protection systems and verification of database registered protection settings to occur annually | Applicable for wind farms. Changes to turbine control parameters will be controlled such that the performance of the generating system and generating units is not compromised in relation to the generator performance standard. Appropriate to use where data is available. | Performance is confirmed by the generating system remaining synchronised during power system disturbance conditions where required under a provision of the Rules. |
|  | - Routine testing of relevant sub-systems including testing by secondary injection all protection system relays, between the generating unit terminals but within the generating system | As appropriate to the technology of the relevant sub-system |  | Performance will be assessed against the performance standard requirements. |
| Protection Systems that Impact on Power System Security (as required under S5.2.5.9 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Routine testing of protection systems including: - CB opening times; - Protection relay injection testing. | As appropriate to the technology of the protection system | Directly measurable | Achieve performance standard |
|  | - Confirmation from fault recorder records of actual performance | Every plant trip |  |  |
|  | Method 2: - Routine testing of relevant sub-systems including: - protection system testing by secondary injection - checking of circuit breaker opening times - redundancy of primary protection systems - timing of trip signal issued by the breaker fail protection system | As appropriate to the technology of the relevant sub-system On every event |  | That all protection relays operate satisfactorily and to within design tolerance of setting value. |
|  | - Assessment of protection system performance in the event of protection system operation |  |  | That protection system is operated in accordance with design and the Performance Standard. |
|  | Method 3: - Performance is monitored, in-service, where data is available. | At each major overhaul; and/or every 5 years by routine functional testing of unit electrical protection systems and verification of database registered protection settings to occur annually | Changes to turbine control parameters will be controlled such that the performance of the generating system and generating units is not compromised in relation to the Generator Performance Standard | Performance is confirmed by assessing operation of protection systems against the requirements of the standard when a generating unit trips as a result of fault occurring between the generating unit stator and the connection point. |
|  | - Relevant testing of any relevant sub-systems including protection system relays shall be tested by secondary injection | As appropriate to the technology of the relevant sub-system |  | Performance will be assessed against the performance standard requirements following a unit trip as a result of a relevant system event in which the unit should have remained synchronised. |
|  | - Verification of database registered protection settings to occur in conjunction with injection testing |  |  |  |
| Asynchronous Operation of Synchronous Generating Units / Protection to Trip Plant for Unstable Operation (as required under S5.2.5.10 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Routine testing of relevant sub-systems including protection system testing by secondary injection | As appropriate to the technology of the relevant sub-system |  | That all protection relays operate satisfactorily and to within design tolerance of setting value. |
|  | - Assessment of protection system performance in the event of protection system operation or of asynchronous operation | On every event |  | That protection system is operated in accordance with design and the Performance Standard. |
| Frequency Control / Frequency Responsiveness and/or Governor Stability and Governor System (as required under: S5.2.5.11 in versions 1-30 of the Rules; S5.2.5.11 and S5.2.6.4 in the initial Code, and all amended versions of the Code before 27 March 2003; and S5.2.5.11 of all amended versions of the Code from 27 March 2003 onwards) | Method 1: Monitor in-service performance using high speed frequency data |  | Appropriate to use where high speed monitors are available and models have been used in establishing compliance | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance only if the models are not available |
|  | Method 2: Assessment of governor system performance during events involving significant variation to system frequency | On every event | Assessment takes into account inertial response, overall governor droop setting etc | That governor system response is within the tolerance specified by the Performance Standards |
|  | Method 3: - Analytical simulation of turbine and governor systems | Type Test permissible where multiple units are involved |  |  |
|  | - Assess generator response to disturbances using high speed recording data | Ongoing |  | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance only if the models are not available |
|  | Method 4: - Step response test of the governor to test damping and droop characteristics | Every 4 years |  | Plant performance complies with the Generator Performance Standard |
|  | - Routine calibration tests | Every 4 years |  |  |
| Stability / Impact on Network Capability (as required under S5.2.5.12 in versions 1-30 of the Rules, and all amended versions of the Code from 27 March 2003 onwards) | Method 1: - Monitor in-service performance for relevant performance characteristics not otherwise tested | Following plant changes | Generator can only be held responsible for ensuring the performance of their generating system as it contributes to meeting this standard | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available |
|  | - Routine monitoring and testing of relevant sub-systems including suitable testing to confirm power system stabiliser performance (if relevant) | As appropriate to the technology of the relevant sub-system |  |  |
| Excitation Control System / Voltage and Reactive Power Control (as required under: S5.2.5.13 in versions 1-30 of the Rules; S5.2.5.13 and S5.2.6.5 in the initial Code, and all amended versions of the Code before 27 March 2003; and S5.2.5.13 of all amended versions of the Code from 27 March 2003 onwards) | Method 1: - Transfer function measurements and step response tests with the unit unsynchronised and at full load | Every 4 years |  | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available |
|  | - Assess the stability of limiter operation |  |  |  |
|  | - Monitoring in-service performance or undertake transfer function measurements |  |  |  |
|  | Method 2: - AVR step response tests | Every 4 years |  | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available |
|  | - AVR step response test of OEL and UEL operation |  |  |  |
|  | - AVR and PSS transfer function measurements over required frequency range |  |  |  |
|  | Method 3: Performance of relevant sub-systems will be monitored using the following systems: digital protection relays; other data-logging equipment as required | As appropriate to the technology of the relevant sub-system | Applicable for Wind Farms. Changes to turbine control parameters will be controlled such that the performance of the generating system and generating units is not compromised in relation to the Generator Performance Standard. | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available |
| Active Power Control (as required under S5.2.5.14 in versions 13-30 of the Rules) | Method 1: One-off installation | Following plant change |  | Achieve performance standard |
|  | Method 2: Monitor non-compliance with dispatch market systems |  |  | Achieve performance standard |
| Remote Monitoring (as required under S5.2.6.1 in versions 1-30 of the Rules, the initial Code, and all amended versions of the Code) | Method 1: - Calibration of Transducers | Following plant change and every 5 years |  | Confirmation at each end of the communications system by both parties |
|  | - Verification of the accuracy of transmitted data |  |  |  |
|  | Method 2: - SCADA monitored values and farm panel metering will be routinely checked | Every 5 years | Applicable for Wind Farms | Achieve performance standard |
|  | - The calibration of transducers and Wind Farm panel metering will be checked | At each major outage or once every 5 years |  |  |
| Communications Equipment (as required under: S5.2.6.3 in versions 1-12 of the Rules, and S5.2.6.2 in versions 13-30 of the Rules; and S5.2.6.3 of the initial Code, and all amended versions of the Code) | Method 1: - Confirmation of the availability of communication links, including any backup links with AEMO | Annual |  | Achieve performance standard |
|  | - Testing of relevant sub-systems including any power backup or UPS system | As appropriate to the technology of the relevant sub-system |  |  |
| Power Station Auxiliary Transformers / Supplies (as required under: S5.2.8 in versions 1-12 of the Rules, and S5.2.7 in versions 13-30 of the Rules; and S5.2.8 of the initial Code, and all amended versions of the Code) | Method 1: - Metering of active and reactive power at the auxiliary supply connection point | Every 4 years | Only applicable when auxiliary supplies are taken from some other point different to generator connection point. Access Standards must be established under clause S5.3.5. | Power factor, quality of supply and protection and control requirements within allowable range / specification |
|  | - Testing of any relevant sub-systems including capacitor banks and circuit breakers | As appropriate to the technology of the relevant sub-system |  | Performance to specification |
|  | Method 2: Performance will be monitored as part of condition monitoring and maintenance routines |  | This standard only applies to generating systems that takes auxiliary supplies from a separate supply. Unit auxiliary supplies on wind farms are taken from within connection point when units are on-line. Very small wind farm station service auxiliary load requirements are considered negligible under NEM CMP requirements. | Achieve performance standard |
| Fault Level / Current (as required under: S5.2.9 in versions 1-12 of the Rules, and S5.2.8 in versions 13-30 of the Rules; and S5.2.9 in all amended versions of the Code from 27 March 2003 onwards) | Method 1: - Monitoring in-service performance during faults near the connection point | Review following any event |  | Calculation confirms current fault current contribution |
|  | - Review and recalculation of fault levels | Following plant change |  |  |
|  | - Routine testing of any relevant sub-systems | As appropriate to the technology of the relevant sub-system |  |  |
|  | Method 2: - Modelling and simulation of plant characteristics to make sure the plant is capable of meeting agreed standards | Following plant change |  | Calculation confirms current fault current contribution |
|  | - Monitoring of generator contribution on fault event | Review following any event |  |  |
|  | Method 3: - Performance of relevant sub-systems will be monitored using the following systems: digital protection relays; other data-logging equipment as required | As appropriate to the technology of the relevant sub-system |  | Achieve performance standard. |
|  | - Where recorded data is available, comparison to be made of measured fault currents and computer simulations | Following a fault |  | Consistency of operation with plant models used to establish initial compliance if the models are available; OR consistency with past performance if the models are not available. |
|  | - Review and recalculation of fault levels | Following plant change |  |  |

This provision was amended in the Code on 9 August 2001 and on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in version 13 of the Rules.

This provision was amended in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.

This provision was amended in the Code on 27 March 2003, and in version 13 of the Rules.